## Inch-Pound
Change the values in the cells that are highlighted in yellow to estimate cable fill values for different diameter cables or fill ratios.
Estimated Cable Fill Capacities for CPI Cable Management and Pathway Products
| Part Number | Description | Cable Manager Specs. |  |  |  | Recommended Fill |  |  | Maximum Cable Fill |  |  | Recommended Cable Fill | [5 empty] | Maximum Cable Fill
|  |  | Interior Width (in.) | Interior Depth (in.) | Usable Area (sq. in.) | Cable | Cat 5e | Cat 6 | Cat 6a | Cat 5e | Cat 6 | Cat 6a
[6 empty] | OD (in.) | 0.2 | 0.25 | 0.3 | 0.2 | 0.25 | 0.3 | 0.2 |  | 0.25 |  | 0.3 |  | 0.2 |  | 0.25 |  | 0.3
[6 empty] | Fill (%) | 50% | 50% | 50% | 100% | 100% | 100% | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
Vertical Cable Managers for Racks
11374 | 11374-XXX | SS Wide Vertical Cable Section, 6"W | 5.6 | 6.0 | 33.6 |  | 267 | 171 | 119 | 535 | 342 | 238 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11378 | 11378-X02 | Extension, SS Narrow Vertical Cable Section, 2'H x 3.65"W | 3.5 | 6.0 | 21 |  | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11378 | 11378-X01 | Extension, SS Wide Vertical Cable Section, 2'H x 6"W | 5.6 | 6.0 | 33.6 |  | 267 | 171 | 119 | 535 | 342 | 238 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11584 | 11584-X02 | Extension, SS Narrow Vertical Cable Section, 1'H x 3.65"W | 3.5 | 6.0 | 21 |  | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11584 | 11584-X01 | Extension, SS Wide Vertical Cable Section, 1'H x 6"W | 5.6 | 6.0 | 33.6 |  | 267 | 171 | 119 | 535 | 342 | 238 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11729 | 11729-XXX | DS Wide Vertical Cable Sect, 6"W (Front/Rear) | 5.7 | 6.0 | 34.2 | Front | 272 | 174 | 121 | 544 | 348 | 242 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11729 |  |  | 5.7 | 6.0 | 34.2 | Rear | 272 | 174 | 121 | 544 | 348 | 242 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11730 | 11730-XXX | SS Narrow Vertical Cable Section, 3.65"W | 3.5 | 6.0 | 21 |  | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11781 | 11781-X02 | Extension, DS Narrow Vertical Cabling Section, 1'H x 3.65"W (Front/Rear) | 3.5 | 6.0 | 21 | Front | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11781 |  |  | 3.5 | 6.0 | 21 | Rear | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11781 | 11781-X01 | Extension, DS Wide Vertical Cabling Section, 1'H x 6"W (Front/Rear) | 5.7 | 6.0 | 34.2 | Front | 272 | 174 | 121 | 544 | 348 | 242 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11781 |  |  | 5.7 | 6.0 | 34.2 | Rear | 272 | 174 | 121 | 544 | 348 | 242 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11782 | 11782-X02 | Extension, DS Narrow Vertical Cabling Section, 2'H x 3.65"W (Front/Rear) | 3.5 | 6.0 | 21 | Front | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11782 |  |  | 3.5 | 6.0 | 21 | Rear | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11782 | 11782-X01 | Extension, DS Wide Vertical Cabling Section, 2'H x 6"W (Front/Rear) | 5.7 | 6.0 | 34.2 | Front | 272 | 174 | 121 | 544 | 348 | 242 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11782 |  |  | 5.7 | 6.0 | 34.2 | Rear | 272 | 174 | 121 | 544 | 348 | 242 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12096 | 12096-XXX | DS Narrow Vertical Cable Sect, 3.65"W (Front/Rear) | 3.5 | 6.0 | 21 | Front | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12096 |  |  | 3.5 | 6.0 | 21 | Rear | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12830-X03 | SS Global Vertical Cabling Section, 3.65"W X 6.76"D, 7'H | 3.1 | 5.5 | 17 |  | 135 | 87 | 60 | 271 | 173 | 120 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12831-X03 | SS Global Vertical Cabling Section, 6"W X 6.76"D, 7'H | 5.4 | 5.5 | 29.7 |  | 236 | 151 | 105 | 473 | 303 | 210 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12832-X03 | SS Global Vertical Cabling Section, 3.65"W X 9.30"D, 7'H | 3.1 | 8 | 24.8 |  | 197 | 126 | 88 | 395 | 253 | 175 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12833-X03 | SS Global Vertical Cabling Section, 6"W X 9.30"D, 7'H | 5.4 | 8 | 43.2 |  | 344 | 220 | 153 | 688 | 440 | 306 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12834-X03 | SS Global Vertical Cabling Section, 10"W X 6.76"D, 7'H | 9.4 | 5.5 | 51.7 |  | 411 | 263 | 183 | 823 | 527 | 366 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12835-X03 | SS Global Vertical Cabling Section, 10"W X 9.30"D, 7'H | 9.4 | 8 | 75.2 |  | 598 | 383 | 266 | 1197 | 766 | 532 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12836-X01 | Global Vertical Cabling Section, Ring Set, 3.65"W X 6.38"D, 7 EA | 3.5 | 6.0 | 21 |  | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12836-X02 | Global Vertical Cabling Section, Ring Set, 6"W X 6.38"D, 7 EA | 5.8 | 6.0 | 34.8 |  | 277 | 177 | 123 | 554 | 354 | 246 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 12836-X03 | Global Vertical Cabling Section, Ring Set, 10"W X 6.38"D, 7 EA | 9.8 | 6.0 | 58.8 |  | 468 | 299 | 208 | 936 | 599 | 416 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13901-7XX | DS Global Vertical Cabling Section, 3.65"W X 13.52"D, 7'H | Varies | 7.5 | 18.5 |  | 147 | 94 | 65 | 294 | 188 | 131 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13902-7XX | Velocity Single-Sided Vertical Cable Manager, 6"W x 9.8"D | Varies | 7.5 | 37 |  | 294 | 188 | 131 | 589 | 377 | 262 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13904-7XX | Velocity Single-Sided Vertical Cable Manager, 10"W x 10.3"D | Varies | 7.5 | 67.7 |  | 539 | 345 | 239 | 1077 | 690 | 479 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13905-7XX | Velocity Single-Sided Vertical Cable Manager, 12"W x 10.4"D | Varies | 7.5 | 83.1 |  | 661 | 423 | 294 | 1323 | 846 | 588 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 | 13911-7XX | Velocity Double-Sided Vertical Cable Manager, 3.6"W x 16.4"D | Varies | 7.5 | 18.5 | Front | 147 | 94 | 65 | 294 | 188 | 131 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 |  |  | Varies | 5.5 | 13.7 | Rear | 109 | 70 | 48 | 218 | 140 | 97 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 | 13912-7XX | Velocity Double-Sided Vertical Cable Manager, 6"W x 16.6"D | Varies | 7.5 | 37 | Front | 294 | 188 | 131 | 589 | 377 | 262 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 |  |  | Varies | 5.5 | 27.2 | Rear | 216 | 139 | 96 | 433 | 277 | 192 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 | 13914-7XX | Velocity Double-Sided Vertical Cable Manager, 10"W x 17.5"D | Varies | 7.5 | 67.7 | Front | 539 | 345 | 239 | 1077 | 690 | 479 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 |  |  | Varies | 5.5 | 49.7 | Rear | 395 | 253 | 176 | 791 | 506 | 352 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 | 13915-7XX | Velocity Double-Sided Vertical Cable Manager, 12"W x 17.8"D | Varies | 7.5 | 83.1 | Front | 661 | 423 | 294 | 1323 | 846 | 588 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 |  |  | Varies | 5.5 | 60.9 | Rear | 485 | 310 | 215 | 969 | 620 | 431 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13934-71X | Velocity Cable Ring Kits, 3.6"W | 3.4 | 6.8 | 23.1 |  | 184 | 118 | 82 | 368 | 235 | 163 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13934-72X | Velocity Cable Ring Kits, 6"W | 5.8 | 6.8 | 39.4 |  | 314 | 201 | 139 | 627 | 401 | 279 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13934-74X | Velocity Cable Ring Kits, 10"W | 9.8 | 6.8 | 66.6 |  | 530 | 339 | 236 | 1060 | 678 | 471 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 13934-75X | Velocity Cable Ring Kits, 12"W | 11.8 | 6.8 | 80.2 |  | 638 | 408 | 284 | 1276 | 817 | 567 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11782 | 14830-X03 | DS Global Vertical Cabling Section, 3.65"W X 13.52"D, 7'H | 3.1 | 5.4 | 16.7 | Front | 133 | 85 | 59 | 266 | 170 | 118 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11782 |  |  | 3.1 | 5.4 | 16.7 | Rear | 133 | 85 | 59 | 266 | 170 | 118 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12096 | 14831-X03 | DS Global Vertical Cabling Section, 6"W X 13.52"D, 7'H | 5.4 | 5.4 | 29.1 | Front | 232 | 148 | 103 | 463 | 296 | 206 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12096 |  |  | 5.4 | 5.4 | 29.1 | Rear | 232 | 148 | 103 | 463 | 296 | 206 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12096 | 14832-X03 | DS Global Vertical Cabling Section, 10"W X 13.52"D, 7'H | 9.4 | 5.4 | 50.7 | Front | 403 | 258 | 179 | 807 | 516 | 359 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12096 |  |  | 9.4 | 5.4 | 50.7 | Rear | 403 | 258 | 179 | 807 | 516 | 359 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30091 | 30091-XXX | SS MCS Master Cabling Section, 4.4"W | Varies | 6.7 | 24.4 |  | 194 | 124 | 86 | 388 | 249 | 173 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30092 | 30092-XXX | SS MCS Master Cabling Section, 6"W | Varies | 6.7 | 35.2 |  | 280 | 179 | 124 | 560 | 359 | 249 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30093 | 30093-XXX | SS MCS Master Cabling Section, 10"W | Varies | 6.7 | 62.3 |  | 496 | 317 | 220 | 992 | 635 | 441 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30094 | 30094-XXX | DS MCS Master Cabling Section, 4.4"W (Front/Rear) | Varies | 6.7 | 24.2 | Front | 193 | 123 | 86 | 385 | 246 | 171 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30094 |  |  | Varies | 6.7 | 24.2 | Rear | 193 | 123 | 86 | 385 | 246 | 171 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30095 | 30095-XXX | DS MCS Master Cabling Section, 6"W (Front/Rear) | Varies | 6.7 | 35.1 | Front | 279 | 179 | 124 | 559 | 358 | 248 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30095 |  |  | Varies | 6.7 | 35.1 | Rear | 279 | 179 | 124 | 559 | 358 | 248 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30096 | 30096-XXX | DS MCS Master Cabling Section, 10"W (Front/Rear) | Varies | 6.7 | 62.3 | Front | 496 | 317 | 220 | 992 | 635 | 441 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30096 |  |  | Varies | 6.7 | 62.3 | Rear | 496 | 317 | 220 | 992 | 635 | 441 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30161 | 30161-7XX | CCS Combination Cabling Section for 3"D Rack, 3.65"W (Front/Rear) | 3.2 | 5.2 | 16.6 | Front | 132 | 85 | 59 | 264 | 169 | 117 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30161 |  |  | 3.2 | 5.2 | 16.6 | Rear | 132 | 85 | 59 | 264 | 169 | 117 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30162 | 30162-7XX | CCS Combination Cabling Section for 3"D Rack, 6"W (Front/Rear) | 5.6 | 5.2 | 29.1 | Front | 232 | 148 | 103 | 463 | 296 | 206 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30162 |  |  | 5.6 | 5.2 | 29.1 | Rear | 232 | 148 | 103 | 463 | 296 | 206 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30163 | 30163-7XX | CCS Combination Cabling Section for 3"D Rack, 10"W (Front/Rear) | 9.6 | 5.2 | 49.9 | Front | 397 | 254 | 176 | 794 | 508 | 353 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30163 |  |  | 9.6 | 5.2 | 49.9 | Rear | 397 | 254 | 176 | 794 | 508 | 353 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30164 | 30164-7XX | CCS Combination Cabling Section for 6"D Rack, 3.65"W (Front/Rear) | 3.2 | 6.7 | 21.4 | Front | 170 | 109 | 76 | 341 | 218 | 151 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30164 |  |  | 3.2 | 6 | 19.2 | Rear | 153 | 98 | 68 | 306 | 196 | 136 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30165 | 30165-7XX | CCS Combination Cabling Section for 6"D Rack, 6"W (Front/Rear) | 5.6 | 6.7 | 37.5 | Front | 298 | 191 | 133 | 597 | 382 | 265 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30165 |  |  | 5.6 | 6 | 33.6 | Rear | 267 | 171 | 119 | 535 | 342 | 238 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30166 | 30166-7XX | CCS Combination Cabling Section for 6"D Rack, 10"W (Front/Rear) | 9.6 | 6.7 | 64.3 | Front | 512 | 327 | 227 | 1023 | 655 | 455 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30166 |  |  | 9.6 | 6 | 57.6 | Rear | 458 | 293 | 204 | 917 | 587 | 407 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32573-X00 | Cable Ring Kit for 6"W (150 mm) Motive Single-Sided Vertical Cable Manager | 5.55 | 8.47 | 47 |  | 374 | 239 | 166 | 748 | 479 | 332 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32573-X01 | Cable Ring Kit for 8"W (200 mm) Motive Single-Sided Vertical Cable Manager | 7.55 | 8.47 | 63.9 |  | 508 | 325 | 226 | 1017 | 651 | 452 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32573-X02 | Cable Ring Kit for 10"W (250 mm) Motive Single-Sided Vertical Cable Manager | 9.55 | 8.47 | 80.8 |  | 643 | 412 | 286 | 1286 | 823 | 572 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32573-X03 | Cable Ring Kit for 12"W (300 mm) Motive Single-Sided Vertical Cable Manager | 11.55 | 8.47 | 97.8 |  | 778 | 498 | 346 | 1557 | 996 | 692 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32573-X04 | Cable Ring Kit for 15"W (380 mm) Motive Single-Sided Vertical Cable Manager | 14.55 | 8.47 | 123.2 |  | 980 | 627 | 436 | 1961 | 1255 | 871 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32610-XXX | Motive Single-Sided Vertical Cable Manager, 6"W x 15.5"D | Varies | 11.5 | 43.7 |  | 348 | 223 | 155 | 696 | 445 | 309 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32611-XXX | Motive Single-Sided Vertical Cable Manager, 8"W x 15.5"D | Varies | 11.5 | 66.7 |  | 531 | 340 | 236 | 1062 | 679 | 472 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32612-XXX | Motive Single-Sided Vertical Cable Manager, 10"W x 15.5"D | Varies | 11.5 | 89.7 |  | 714 | 457 | 317 | 1428 | 914 | 634 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32613-XXX | Motive Single-Sided Vertical Cable Manager, 12"W x 15.5"D | Varies | 11.5 | 112.7 |  | 897 | 574 | 399 | 1794 | 1148 | 797 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32614-XXX | Motive Single-Sided Vertical Cable Manager, 15"W x 15.5"D | Varies | 11.5 | 147.2 |  | 1171 | 750 | 521 | 2343 | 1499 | 1041 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32620-XXX | Motive Double-Sided Vertical Cable Manager, 6"W x 23.6"D (Front/Rear) | Varies | 8.7 | 33 | Front | 263 | 168 | 117 | 525 | 336 | 233 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
|  |  | Varies | 8.7 | 33 | Rear | 263 | 168 | 117 | 525 | 336 | 233 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32621-XXX | Motive Double-Sided Vertical Cable Manager, 8"W x 23.6"D (Front/Rear) | Varies | 8.7 | 50.4 | Front | 401 | 257 | 178 | 802 | 513 | 357 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
|  |  | Varies | 8.7 | 50.4 | Rear | 401 | 257 | 178 | 802 | 513 | 357 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32622-XXX | Motive Double-Sided Vertical Cable Manager, 10"W x 23.6"D (Front/Rear) | Varies | 8.7 | 67.8 | Front | 540 | 345 | 240 | 1079 | 691 | 480 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
|  |  | Varies | 8.7 | 67.8 | Rear | 540 | 345 | 240 | 1079 | 691 | 480 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32623-XXX | Motive Double-Sided Vertical Cable Manager, 12"W x 23.6"D (Front/Rear) | Varies | 8.7 | 85.2 | Front | 678 | 434 | 301 | 1356 | 868 | 603 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
|  |  | Varies | 8.7 | 85.2 | Rear | 678 | 434 | 301 | 1356 | 868 | 603 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32624-XXX | Motive Double-Sided Vertical Cable Manager, 15"W x 23.6"D (Front/Rear) | Varies | 8.7 | 111.3 | Front | 886 | 567 | 394 | 1771 | 1134 | 787 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
|  |  | Varies | 8.7 | 111.3 | Rear | 886 | 567 | 394 | 1771 | 1134 | 787 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40092 | 35475-701 | Evolution Fiber Segregation Kit | 2.4 | 4 | 9.6 |  | 76 | 49 | 34 | 153 | 98 | 68 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 33544-705 | Evolution II Fiber Segregation Kit | 2.4 | 4 | 9.6 |  | 76 | 49 | 34 | 153 | 98 | 68
40092 | 35511-XXX | Evolution Single-Sided Vertical Cable Manager, 6"W x 13.2"D | Varies | 10.6 | 49.5 | Front | 394 | 252 | 175 | 788 | 504 | 350 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40092 | 35512-XXX | Evolution Single-Sided Vertical Cable Manager, 8"W x 13.2"D | Varies | 10.6 | 70.6 | Front | 562 | 360 | 250 | 1124 | 719 | 499 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40093 | 35513-XXX | Evolution Single-Sided Vertical Cable Manager, 10"W x 13.2"D | Varies | 10.6 | 91.7 | Front | 730 | 467 | 324 | 1459 | 934 | 649 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40094 | 35514-XXX | Evolution Single-Sided Vertical Cable Manager, 12"W x 13.2"D | Varies | 10.6 | 112.9 | Front | 898 | 575 | 399 | 1797 | 1150 | 799 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40094 | 35515-XXX | Evolution Single-Sided Vertical Cable Manager, 15"W x 13.2"D | Varies | 10.6 | 144.6 | Front | 1151 | 736 | 511 | 2301 | 1473 | 1023 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 | 35521-XXX | Evolution Double-Sided Vertical Cable Manager, 6"W x 24.5"D, (40%, 50%, 60% of Front/Rear) | Varies | 7.5 | 36.9 | 40% | 294 | 188 | 131 | 587 | 376 | 261 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 |  |  | Varies | 10.1 | 46.1 | 50% | 367 | 235 | 163 | 734 | 470 | 326 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 |  |  | Varies | 12.6 | 55.4 | 60% | 441 | 282 | 196 | 882 | 564 | 392 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 | 35522-XXX | Evolution Double-Sided Vertical Cable Manager, 8"W x 24.5"D, (40%, 50%, 60% of Front/Rear) | Varies | 7.5 | 53 | 40% | 422 | 270 | 187 | 844 | 540 | 375 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 |  |  | Varies | 10.1 | 66.3 | 50% | 528 | 338 | 234 | 1055 | 675 | 469 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 |  |  | Varies | 12.6 | 79.6 | 60% | 633 | 405 | 282 | 1267 | 811 | 563 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40096 | 35523-XXX | Evolution Double-Sided Vertical Cable Manager, 10"W x 24.5"D, (40%, 50%, 60% of Front/Rear) | Varies | 7.5 | 69.2 | 40% | 551 | 352 | 245 | 1101 | 705 | 489 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40096 |  |  | Varies | 10.1 | 86.4 | 50% | 688 | 440 | 306 | 1375 | 880 | 611 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40096 |  |  | Varies | 12.6 | 103.7 | 60% | 825 | 528 | 367 | 1650 | 1056 | 734 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 35524-XXX | Evolution Double-Sided Vertical Cable Manager, 12"W x 24.5"D, (40%, 50%, 60% of Front/Rear) | Varies | 7.5 | 85.3 | 40% | 679 | 434 | 302 | 1358 | 869 | 603 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | Varies | 10.1 | 106.6 | 50% | 848 | 543 | 377 | 1697 | 1086 | 754 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | Varies | 12.6 | 127.9 | 60% | 1018 | 651 | 452 | 2036 | 1303 | 905 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 35525-XXX | Evolution Double-Sided Vertical Cable Manager, 15"W x 24.5"D, (40%, 50%, 60% of Front/Rear) | Varies | 7.5 | 109.4 | 40% | 871 | 557 | 387 | 1741 | 1114 | 774 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | Varies | 10.1 | 136.8 | 50% | 1089 | 697 | 484 | 2177 | 1393 | 968 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | Varies | 12.6 | 164.2 | 60% | 1307 | 836 | 581 | 2613 | 1673 | 1161 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 35571-XXX | Evolution Combination Vertical Cable Manager, 6"W x 20.2"D | Varies | 10.1 | 49.5 | Front | 394 | 252 | 175 | 788 | 504 | 350 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | 5.5 | 5.9 | 32.4 | Rear | 258 | 165 | 115 | 516 | 330 | 229 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 35572-XXX | Evolution Combination Vertical Cable Manager, 8"W x 20.2"D | Varies | 10.1 | 70.6 | Front | 562 | 360 | 250 | 1124 | 719 | 499 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | 7.5 | 5.9 | 44.2 | Rear | 352 | 225 | 156 | 703 | 450 | 313 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 35573-XXX | Evolution Combination Vertical Cable Manager, 10"W x 20.2"D | Varies | 10.1 | 91.7 | Front | 730 | 467 | 324 | 1459 | 934 | 649 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | 9.5 | 5.9 | 56 | Rear | 446 | 285 | 198 | 891 | 570 | 396 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 35574-XXX | Evolution Combination Vertical Cable Manager, 12"W x 20.2"D | Varies | 10.1 | 112.9 | Front | 898 | 575 | 399 | 1797 | 1150 | 799 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | 11.5 | 5.9 | 67.8 | Rear | 540 | 345 | 240 | 1079 | 691 | 480 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 35575-XXX | Evolution Combination Vertical Cable Manager, 15"W x 20.2"D | Varies | 10.1 | 144.6 | Front | 1151 | 736 | 511 | 2301 | 1473 | 1023 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | 14.5 | 5.9 | 85.5 | Rear | 680 | 435 | 302 | 1361 | 871 | 605 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40092 | 40092-XXX | SS MCS-EFX Master Cabling Section With Extended Fingers, 6"W | Varies | 9.3 | 46.1 |  | 367 | 235 | 163 | 734 | 470 | 326 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40093 | 40093-XXX | SS MCS-EFX Master Cabling Section With Extended Fingers, 10"W | Varies | 9.3 | 83.4 |  | 664 | 425 | 295 | 1327 | 850 | 590 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40094 | 40094-XXX | SS MCS-EFX Master Cabling Section With Extended Fingers, 12"W | Varies | 9.3 | 102 |  | 812 | 519 | 361 | 1623 | 1039 | 722 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 | 40095-XXX | DS MCS-EFX Master Cabling Section With Extended Fingers, 6"W (Front/Rear) | Varies | 9.3 | 46.8 | Front | 372 | 238 | 166 | 745 | 477 | 331 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40095 |  |  | Varies | 9.3 | 46.8 | Rear | 372 | 238 | 166 | 745 | 477 | 331 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40096 | 40096-XXX | DS MCS-EFX Master Cabling Section With Extended Fingers, 10"W | Varies | 9.3 | 84.1 | Front | 669 | 428 | 297 | 1338 | 857 | 595 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40096 |  |  | Varies | 9.3 | 84.1 | Rear | 669 | 428 | 297 | 1338 | 857 | 595 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 | 40097-XXX | DS MCS-EFX Master Cabling Section With Extended Fingers, 12"W (Front/Rear) | Varies | 9.3 | 102.8 | Front | 818 | 524 | 364 | 1636 | 1047 | 727 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40097 |  |  | Varies | 9.3 | 102.8 | Rear | 818 | 524 | 364 | 1636 | 1047 | 727 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40098 | 40098-7XX | CCS - EFX Combination Cabling Section With Extended Fingers for 3"D Rack, 6"W (Front/Rear) | 5.4 | 7.8 | 42.1 | Front | 335 | 214 | 149 | 670 | 429 | 298 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40098 |  |  | 5.6 | 5.2 | 29.1 | Rear | 232 | 148 | 103 | 463 | 296 | 206 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40099 | 40099-7XX | CCS - EFX Combination Cabling Section With Extended Fingers for 3"D Rack, 10"W (Front/Rear) | 9.4 | 7.8 | 73.3 | Front | 583 | 373 | 259 | 1167 | 747 | 518 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40099 |  |  | 9.6 | 5.2 | 49.9 | Rear | 397 | 254 | 176 | 794 | 508 | 353 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40100 | 40100-7XX | CCS - EFX Combination Cabling Section With Extended Fingers for 3"D Rack, 12"W (Front/Rear) | 11.4 | 7.8 | 88.9 | Front | 707 | 453 | 314 | 1415 | 906 | 629 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
40100 |  |  | 11.6 | 5.2 | 60.3 | Rear | 480 | 307 | 213 | 960 | 614 | 427 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 57011-703 | Velocity Standard Pack with a Single-Sided Vertical Cable Manager, 3.6"W x 9.7"D | Varies | 7.5 | 18.5 |  | 147 | 94 | 65 | 294 | 188 | 131 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 | 57012-703 | Velocity Standard Pack with a Double-Sided Vertical Cable Manager, 3.6"W x 16.4"D | Varies | 7.5 | 18.5 | Front | 147 | 94 | 65 | 294 | 188 | 131 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 |  |  | Varies | 5.5 | 13.7 | Rear | 109 | 70 | 48 | 218 | 140 | 97 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12836 | 57013-703 | Velocity Standard Pack with a Single-Sided Vertical Cable Manager, 6"W x 9.8"D | Varies | 7.5 | 37 |  | 294 | 188 | 131 | 589 | 377 | 262 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 | 57014-703 | Velocity Standard Pack with a Double-Sided Vertical Cable Manager, 6"W x 16.6"D | Varies | 7.5 | 37 | Front | 294 | 188 | 131 | 589 | 377 | 262 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
14830 |  |  | Varies | 5.5 | 27.2 | Rear | 216 | 139 | 96 | 433 | 277 | 192 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
Vertical Cable Managers for Cabinet Enclosures
34416 | 38647-X11 38647-X14 38647-X17 38647-X21 | Vertical Cable Manager with Long Fingers for 27.6"W (700 mm) ZetaFrame Cabinet | 2.2 | 7.5 | 17 |  | 135 | 87 | 60 | 271 | 173 | 120 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 38647-X22 38647-X25 38647-X28 38647-X32 | Vertical Cable Manager with Long Fingers for 29.5"W (750 mm) ZetaFrame Cabinet | 3.2 | 7.5 | 24.5 |  | 195 | 125 | 87 | 390 | 250 | 173 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 38647-X33 38647-X36 38647-X39 38647-X43 | Vertical Cable Manager with Long Fingers for 31.5"W (800 mm) ZetaFrame Cabinet | 4.2 | 7.5 | 31.9 |  | 254 | 162 | 113 | 508 | 325 | 226 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 39835-X00 39835-X03 39835-X06 39835-X10 | Vertical Cable Manager with Short Fingers for 23.6"W (600 mm) ZetaFrame Cabinet | 0.4 | 5 | 1.8 |  | 14 | 9 | 6 | 29 | 18 | 13 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 38646-X11 38646-X14 38646-X17 38646-X21 | Vertical Cable Manager with Short Fingers for 27.6"W (700 mm) ZetaFrame Cabinet | 2.2 | 5 | 11.2 |  | 89 | 57 | 40 | 178 | 114 | 79 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 38646-X22 38646-X25 38646-X28 38646-X32 | Vertical Cable Manager with Short Fingers for 29.5"W (750 mm) ZetaFrame Cabinet | 3.2 | 5 | 16.2 |  | 129 | 83 | 57 | 258 | 165 | 115 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 38646-X33 38646-X36 38646-X39 38646-X43 | Vertical Cable Manager with Short Fingers for 31.5"W (800 mm) ZetaFrame Cabinet | 4.2 | 5 | 21.2 |  | 169 | 108 | 75 | 337 | 216 | 150 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 38634-XXX | Cable Lashing Panel for ZetaFrame Cabinet, 2-3/4" W | Varies | 1 x 1.5" Ø | 1.4 |  | 11 | 7 | 5 | 22 | 14 | 10 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 38635-XXX | Cable Lashing Panel for ZetaFrame Cabinet, 4.5" W | Varies | 3 x 1.5" Ø | 2.3 |  | 18 | 12 | 8 | 37 | 23 | 16 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 38636-XXX | Cable Lashing Panel for ZetaFrame Cabinet, 7.0" W | Varies | 5 x 1.5" Ø | 3.5 |  | 28 | 18 | 12 | 56 | 36 | 25 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 38648-X01 | Front-to-Rear Cable Manager for 27.6"W (700 mm) ZetaFrame Cabinet | 2.1 | 3.2 | 6.72 |  | 53 | 34 | 24 | 107 | 68 | 48 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 38648-X02 | Front-to-Rear Cable Manager for 29.5"W (750 mm) ZetaFrame Cabinet | 3.1 | 3.2 | 9.9 |  | 79 | 50 | 35 | 158 | 101 | 70 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 38648-X03 | Front-to-Rear Cable Manager for 31.5"W (800 mm) ZetaFrame Cabinet | 4.1 | 3.2 | 13.1 |  | 104 | 67 | 46 | 208 | 133 | 93 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13485 | 13485-XXX | Vertical Cable Manager for Cube-iT Wall-Mount Floor-Supported Cabinet | 2.7 | 4.8 | 12.9 |  | 103 | 66 | 46 | 205 | 131 | 91 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 14440-X0X | Z4 SeismicFrame Ring Cable Manager, 600 mm W | 0.9 | 3.3 | 2.9 |  | 23 | 15 | 10 | 46 | 30 | 21 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 14445-X0X | Z4 SeismicFrame Ring Cable Manager, 800 mm W | 4.2 | 3.5 | 14.7 |  | 117 | 75 | 52 | 234 | 150 | 104 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 14465-X0X | Z4 SeismicFrame Cable Lashing Bracket | 1.6 | 1 x 1.5" Ø | 1.7 |  | 14 | 9 | 6 | 27 | 17 | 12 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25104-001 | GT-Series GlobalFrame, Cable Ring Kit, for 600 mm W cabinets | 1 | 4.4 | 4.4 |  | 35 | 22 | 16 | 70 | 45 | 31 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25106-001 | GT-Series GlobalFrame, Cable Ring Kit, with Large Cable Rings, for 800 mm W cabinets | 4.2 | 8.6 | 36.1 |  | 287 | 184 | 128 | 575 | 368 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25106-002 | GT-Series GlobalFrame, Cable Ring Kit, with Medium Cable Rings, for 800 mm W cabinets | 4.2 | 3.5 | 14.7 |  | 117 | 75 | 52 | 234 | 150 | 104 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25107-001 | GT-Series GlobalFrame, Snap-In Grommet Kit, 1 Grommet | 3.2 | 5.5 | 17.6 |  | 140 | 90 | 62 | 280 | 179 | 124 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25108-001 | GT-Series GlobalFrame, Snap-In Grommet & Plug Kit, 1 Grommet | 3.2 | 5.5 | 17.6 |  | 140 | 90 | 62 | 280 | 179 | 124 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25110-700 | GT-Series GlobalFrame, Vertical Cable Manager, with Standard Fingers, for 42U x 600 mm W Cabinets | 1 | 6.1 | 6.1 |  | 49 | 31 | 22 | 97 | 62 | 43 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25120-706 | GT-Series GlobalFrame, Vertical Cable Manager, with Extended Fingers, for 42U x 800 mm W cabinets | 4.8 | 8.5 | 40.8 |  | 325 | 208 | 144 | 649 | 416 | 289 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25402-700 | GT-Series GlobalFrame, Cable Ring Manager, with Large Cable Rings, for 42U x 800 mm cabinet | 4.2 | 8.6 | 36.1 |  | 287 | 184 | 128 | 575 | 368 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25402-701 | GT-Series GlobalFrame, Cable Ring Manager, with Medium Cable Rings, for 42U x 800 mm cabinet | 4.2 | 3.5 | 14.7 |  | 117 | 75 | 52 | 234 | 150 | 104 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25403-701 | GT-Series GlobalFrame, Cable Lashing Bracket, 42U x 125 mm | 5 | 2 | 10 |  | 80 | 51 | 35 | 159 | 102 | 71 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 25404-706 | GT-Series GlobalFrame, Vertical Cable Manager, with Standard Fingers, for 42U x 800 mm W cabinets | 4.8 | 6.1 | 29.2 |  | 232 | 149 | 103 | 465 | 297 | 207 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13485 | 40970-7XX | Vertical Cable Management Section for CUBE-iT Wall-Mount Cabinet | 1.6 | 5 | 8 |  | 64 | 41 | 28 | 127 | 81 | 57 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13485 | 40971-XXX | Lashing Bracket for CUBE-iT Wall-Mount Cabinet | 1.6 | 4 | 6.4 |  | 51 | 33 | 23 | 102 | 65 | 45 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
Horizontal Cable Managers for Racks and Cabinet Enclosures
11563 | 11563-X01 | Large Horizontal Cable Ring, Individual | 2.8 | 6.0 | 16.8 |  | 134 | 86 | 59 | 267 | 171 | 119 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11564 | 11564-XXX | Large Horizontal Ring Panel, 2U | 2.8 | 6.0 | 16.8 |  | 134 | 86 | 59 | 267 | 171 | 119 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11752 | 11752-XXX | Rack Cable Manager, Small Ring, 1U | 1.2 | 0.9 | 1 |  | 8 | 5 | 4 | 16 | 10 | 7 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11753 | 11753-XXX | Rack Cable Manager, Medium Ring, 2U | 2.5 | 1.2 | 3 |  | 24 | 15 | 11 | 48 | 31 | 21 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12183 | 12183-XXX | Upper Jumper Tray, 2U, 3.5"D | 1.9 | 3.3 | 6.2 |  | 49 | 32 | 22 | 99 | 63 | 44 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12185 | 12185-XXX | Lower Jumper Tray, Single, 2U | 2.0 | 3.3 | 6.6 |  | 53 | 34 | 23 | 105 | 67 | 47 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12186 | 12186-X01 | Transition Plate | 1.9 | 3.3 | 6.2 |  | 49 | 32 | 22 | 99 | 63 | 44 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12187 | 12187-XXX | Lower Jumper Tray, Double, 3U | 3.8 | 3.3 | 12.5 |  | 99 | 64 | 44 | 199 | 127 | 88 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12382 | 12382-XXX | Rack Top Mount Cable Trough, 6"D | 2.0 | 5.8 | 11.6 |  | 92 | 59 | 41 | 185 | 118 | 82 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12383 | 12383-XXX | Rack Top Mount Cable Trough, 9"D | 1.9 | 8.8 | 16.7 |  | 133 | 85 | 59 | 266 | 170 | 118 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12541 | 12541-X19 | 19" Horizontal Wire Management Panel, 1U, w/o Spools | 1.4 | 2.4 | 3.3 |  | 26 | 17 | 12 | 53 | 34 | 23 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12542 | 12542-X19 | 19" Horizontal Wire Management Panel, 2U, w/o Spools | 3.2 | 2.4 | 7.6 |  | 60 | 39 | 27 | 121 | 77 | 54 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13070 | 13070-X19 | 19" Horizontal Wire Management Panel, 1U | 1.4 | 2.4 | 3.3 |  | 26 | 17 | 12 | 53 | 34 | 23 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13075 | 13075-X19 | 19" Horizontal Wire Management Panel, 2U | 3.2 | 2.4 | 7.6 |  | 60 | 39 | 27 | 121 | 77 | 54 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13183 | 13183-XXX | Upper Jumper Tray, 2U, 6"D | 2.9 | 5.8 | 16.8 |  | 134 | 86 | 59 | 267 | 171 | 119 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13517 | 13517-701 | Rack-Mount Cable Shelf (sum of 3 openings) | 0.7 | 11.4 | 8 |  | 64 | 41 | 28 | 127 | 81 | 57 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13517 | 13930-701 | Velocity SS Horizontal Cable Manager, 1U | Varies | 3.2 | 2.9 |  | 23 | 15 | 10 | 46 | 30 | 21 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13517 | 13930-702 | Velocity SS Horizontal Cable Manager, 2U | Varies | 3.2 | 9.7 |  | 77 | 49 | 34 | 154 | 99 | 69 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13517 | 13930-703 | Velocity SS Horizontal Cable Manager, 3U | Varies | 3.2 | 16.5 |  | 131 | 84 | 58 | 263 | 168 | 117 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
34416 | 14485-X00 | Z4 SeismicFrame FTR Cable Manager, 800 mm W | 2.5 | 3 | 7.5 |  | 60 | 38 | 27 | 119 | 76 | 53 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 30130-7XX | Univ Horizontal Cable Manager, 2U | 2.7 | 3.9 | 10.5 |  | 84 | 53 | 37 | 167 | 107 | 74 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30131 | 30131-7XX | Univ Horizontal Cable Manager, 3U | 4.5 | 3.9 | 17.5 |  | 139 | 89 | 62 | 279 | 178 | 124 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30139 | 30139-7XX | Univ Horizontal Cable Manager, 1U | 1.0 | 3.9 | 3.9 |  | 31 | 20 | 14 | 62 | 40 | 28 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30330 | 30330-7XX | Univ Horizontal Cable Manager, 2U, Deep | 2.7 | 5.2 | 14 |  | 111 | 71 | 50 | 223 | 143 | 99 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30331 | 30331-7XX | Univ Horizontal Cable Manager, 3U, Deep | 4.5 | 5.2 | 23.4 |  | 186 | 119 | 83 | 372 | 238 | 166 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30339 | 30339-7XX | Univ Horizontal Cable Manager, 1U, Deep | 1.0 | 5.2 | 5.2 |  | 41 | 26 | 18 | 83 | 53 | 37 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30529 | 30529-7XX | DS Univ Horizontal Cable Manager, 1U (Front/Rear) | 1.0 | 3.9 | 3.9 | Front | 31 | 20 | 14 | 62 | 40 | 28 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30529 |  |  | 0.8 | 6.8 | 5.4 | Rear | 43 | 28 | 19 | 86 | 55 | 38 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30530 | 30530-7XX | DS Univ Horizontal Cable Manager, 2U (Front/Rear) | 2.7 | 3.9 | 10.5 | Front | 84 | 53 | 37 | 167 | 107 | 74 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30530 |  |  | 2.5 | 6.8 | 17 | Rear | 135 | 87 | 60 | 271 | 173 | 120 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30531 | 30531-7XX | DS Univ Horizontal Cable Manager, 3U (Front/Rear) | 4.5 | 3.9 | 17.5 | Front | 139 | 89 | 62 | 279 | 178 | 124 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30531 |  |  | 4.3 | 6.8 | 29.2 | Rear | 232 | 149 | 103 | 465 | 297 | 207 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30540 | 30540-719 | DS Univ Horizontal Cable Manager for Use with CCS and 6" Deep Rack, 2U, 19"W (Front/Rear) | 2.7 | 3.9 | 10.5 | Front | 84 | 53 | 37 | 167 | 107 | 74 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30540 |  |  | 2.6 | 9.2 | 23.9 | Rear | 190 | 122 | 85 | 380 | 243 | 169 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 3543X-X01 | Motive Horizontal Cable Manager, 1U | 0.85 | 6.5 | 5.5 |  | 44 | 28 | 19 | 88 | 56 | 39 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 3543X-X02 | Motive Horizontal Cable Manager, 2U | 2.6 | 6.5 | 17 |  | 135 | 87 | 60 | 271 | 173 | 120 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 3543X-X03 | Motive Horizontal Cable Manager, 3U | 4.3 | 6.5 | 28 |  | 223 | 143 | 99 | 446 | 285 | 198 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 3543X-X04 | Motive Horizontal Cable Manager, 4U | 6.1 | 6.5 | 39.6 |  | 315 | 202 | 140 | 630 | 403 | 280 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 35441-X01 | Evolution Horizontal Cable Manager, 1U | 0.85 | 6.5 | 5.5 |  | 44 | 28 | 19 | 88 | 56 | 39 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 3544X-X02 | Evolution Horizontal Cable Manager, 2U | 2.6 | 6.5 | 17 |  | 135 | 87 | 60 | 271 | 173 | 120 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 3544X-X03 | Evolution Horizontal Cable Manager, 3U | 4.3 | 6.5 | 28 |  | 223 | 143 | 99 | 446 | 285 | 198 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 3544X-X04 | Evolution Horizontal Cable Manager, 4U | 6.1 | 6.5 | 39.6 |  | 315 | 202 | 140 | 630 | 403 | 280 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 33548-X02 | Evolution Horizontal Cable Manager, Brush, 2U | 2.6 | 6.5 | 17 |  | 135 | 87 | 60 | 271 | 173 | 120
| 33548-X03 | Evolution Horizontal Cable Manager, Brush, 3U | 4.3 | 6.5 | 28 |  | 223 | 143 | 99 | 446 | 285 | 198
| 33548-X04 | Evolution Horizontal Cable Manager, Brush, 4U | 6.1 | 6.5 | 39.6 |  | 315 | 202 | 140 | 630 | 403 | 280
| 33549-X02 | Evolution Horizontal Cable Manager, Grommet, 2U | 2.6 | 6.5 | 17 |  | 135 | 87 | 60 | 271 | 173 | 120
| 33549-X03 | Evolution Horizontal Cable Manager, Grommet, 3U | 4.3 | 6.5 | 28 |  | 223 | 143 | 99 | 446 | 285 | 198
| 33549-X04 | Evolution Horizontal Cable Manager, Grommet, 4U | 6.1 | 6.5 | 39.6 |  | 315 | 202 | 140 | 630 | 403 | 280
30130 | 39077-X00 | Front-to-Rear Cable Manager | 2.5 | 3 | 7.5 |  | 60 | 38 | 27 | 119 | 76 | 53 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 39377-X01 | Front-to-Rear Cable Manager | 2.5 | 2.6 | 6.5 |  | 52 | 33 | 23 | 103 | 66 | 46 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
30130 | 39377-X02 | Telescoping Cable Manager, for 1016mm N-Series | 6.8 | 3.3 | 22.44 |  | 179 | 114 | 79 | 357 | 229 | 159 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
Individual Cable Management Loops, Rings, Clips, Guides, and Cable Ties
2006 | 02006-2XX | Safe-T-Grip, Open, 6"L | 2" Ø | N/A | 3.1 |  | 25 | 16 | 11 | 49 | 32 | 22 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
2009 | 02009-2XX | Safe-T-Grip, Open, 9"L | 3" Ø | N/A | 7 |  | 56 | 36 | 25 | 111 | 71 | 50 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
2012 | 02012-2XX | Safe-T-Grip, Open, 12"L | 4" Ø | N/A | 12.5 |  | 99 | 64 | 44 | 199 | 127 | 88 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
5006 | 05006-2XX | Safe-T-Grip, End, 6"L | 2" Ø | N/A | 3.1 |  | 25 | 16 | 11 | 49 | 32 | 22 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
5009 | 05009-2XX | Safe-T-Grip, End, 9"L | 3" Ø | N/A | 7 |  | 56 | 36 | 25 | 111 | 71 | 50 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
5012 | 05012-2XX | Safe-T-Grip, End, 12"L | 4" Ø | N/A | 12.5 |  | 99 | 64 | 44 | 199 | 127 | 88 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
6006 | 06006-2XX | Safe-T-Grip, Center, 6"L | 2" Ø | N/A | 3.1 |  | 25 | 16 | 11 | 49 | 32 | 22 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
6009 | 06009-2XX | Safe-T-Grip, Center, 9"L | 3" Ø | N/A | 7 |  | 56 | 36 | 25 | 111 | 71 | 50 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
6012 | 06012-2XX | Safe-T-Grip, Center, 12"L | 4" Ø | N/A | 12.5 |  | 99 | 64 | 44 | 199 | 127 | 88 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10419 | 10419-001 | Horizontal Cable Guide, 1 Loop (Per Loop) | 2.5 | 3.3 | 8.2 |  | 65 | 42 | 29 | 131 | 84 | 58 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10683 | 10683-001 | IBM Style Vertical Cable Loop | 2.2 | 3.8 | 8.3 |  | 66 | 42 | 29 | 132 | 85 | 59 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11125 | 11125-0XX | Channel-Mounted Distrib Ring, 3"W | 2.6 | 3.0 | 7.8 |  | 62 | 40 | 28 | 124 | 79 | 55 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11153 | 11153-001 | Horizontal Cable Guide, 6 Loop (Per Loop) | 2.6 | 2.0 | 5.2 |  | 41 | 26 | 18 | 83 | 53 | 37 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11154 | 11154-001 | Horizontal Cable Guide, 4 Loop (Per Loop) | 2.6 | 1.5 | 3.9 |  | 31 | 20 | 14 | 62 | 40 | 28 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11157 | 11157-001 | Horizontal Cable Guide, 2 Loop (Per Loop) | 2.6 | 1.9 | 4.9 |  | 39 | 25 | 17 | 78 | 50 | 35 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11225 | 11228-X01 | Narrow Cable Ring | 1.1 | 3.8 | 4.1 |  | 33 | 21 | 15 | 65 | 42 | 29 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11225 | 11230-X01 | Narrow Cable Loop | 1.1 | 3.8 | 4.1 |  | 33 | 21 | 15 | 65 | 42 | 29 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11228 | 11799-001 | Cable Loop for Swing Gate, 6PK | 3" Ø | N/A | 7 |  | 56 | 36 | 25 | 111 | 71 | 50 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11230 | 12228-X01 | Double-Wide Cable Ring | 2.6 | 3.8 | 9.8 |  | 78 | 50 | 35 | 156 | 100 | 69 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11799 | 12340-701 | Horizontal Cable Guide. 4U (Per U) | 1.4 | 3.6 | 5 |  | 40 | 25 | 18 | 80 | 51 | 35 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12210 | 12341-701 | Horizontal Cable Guide, 2U (Per U) | 1.3 | 3.6 | 4.6 |  | 37 | 23 | 16 | 73 | 47 | 33 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12228 | 12370-00X | Finger Snaps Cable Guides, 6 Loop (Per Loop) | Varies | 2.4 | 3.1 |  | 25 | 16 | 11 | 49 | 32 | 22 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12340 | 12891-70X | Extended Finger Bracket (Per U) | Varies | 5.8 | 6.6 |  | 53 | 34 | 23 | 105 | 67 | 47 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12341 | 13079-001 | Vertical Wire Management Loop | 2.3 | 3.1 | 7.1 |  | 56 | 36 | 25 | 113 | 72 | 50 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12370 | Wall-Mount Cable Management Rings | [11 empty] | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12891 | 10812-001 | Closed Composite Distrib Ring, 3"W | 2.8 | 3.1 | 8.6 |  | 68 | 44 | 30 | 137 | 88 | 61 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13079 | 10900-500 | Wall Cable Support Bracket, 10"H x 6"D | 5.8 | 5.9 | 34.2 |  | 272 | 174 | 121 | 544 | 348 | 242 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 10910-500 | Wall Cable Support Bracket, 8"H x 4"D | 3.9 | 3.9 | 15.2 |  | 121 | 77 | 54 | 242 | 155 | 108 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10812 | 10920-500 | Wall Cable Support Bracket, 12"H x 4"D | 7.5 | 3.9 | 29.2 |  | 232 | 149 | 103 | 465 | 297 | 207 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10900 | 10921-500 | Wall Cable Support Bracket, 8"H x 4"D | 3.8 | 3.9 | 14.8 |  | 118 | 75 | 52 | 236 | 151 | 105 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10941 | 11322-106 | J-Hook Ceiling Cable Bracket, 6"H x 3"D | 2.0 | 2.8 | 5.6 |  | 45 | 29 | 20 | 89 | 57 | 40 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10942 | 11322-112 | J-Hook Ceiling Cable Bracket, 12"H x 3"D | 2.0 | 2.8 | 5.6 |  | 45 | 29 | 20 | 89 | 57 | 40 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10943 | 11322-118 | J-Hook Ceiling Cable Bracket, 18"H x 3"D | 2.0 | 2.8 | 5.6 |  | 45 | 29 | 20 | 89 | 57 | 40 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11322 | 12035-001 | Open Composite Distrib Ring, 2"W | 2.6 | 2.0 | 5.2 |  | 41 | 26 | 18 | 83 | 53 | 37 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11322 | 12127-001 | Closed Composite Distrib Ring, 2"W | 1.9 | 2.1 | 3.9 |  | 31 | 20 | 14 | 62 | 40 | 28 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11322 | Raised Floor Grommets | [11 empty] | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12035 | 13671-00X | Raised Floor Grommet | 8.0 | 4.15 | 33.2 |  | 264 | 169 | 117 | 528 | 338 | 235 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12035 | 13874-00X | 4" Round Raised Floor Grommet | 4.0 Ø | N/A | 6.6 |  | 53 | 34 | 23 | 105 | 67 | 47 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13677 | Miscellaneous Rack, Cabinet and Cable Management Cable Openings | [11 empty] | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 46XXX-XXX | Universal Rack, Interior of Mounting Channel | 0.6 | 2.5 | 1.5 |  | 12 | 8 | 5 | 24 | 15 | 11 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
13571 | 48XXX-XXX | Universal Rack, Interior of Mounting Channel | 0.6 | 2.5 | 1.5 |  | 12 | 8 | 5 | 24 | 15 | 11 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 55053-XXX | Standard Rack, Interior of Mounting Channel | 1.1 | 2.6 | 2.8 |  | 22 | 14 | 10 | 45 | 29 | 20 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 663XX-XXX | 6" Deep Standard Rack, Interior of Management Channel | 1.0 | 5.6 | 5.6 |  | 45 | 29 | 20 | 89 | 57 | 40 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 663XX-XXX | 6" Deep Standard Rack, Interior of Management Channel | 1.0 | 5.6 | 5.6 |  | 45 | 29 | 20 | 89 | 57 | 40 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| ZXXX-XXXXX-XX | ZetaFrame, Cable Port Opening for Top and Bottom Panels With Grommet, Each | 3.9 | 8.8 | 34.32 |  | 273 | 175 | 121 | 546 | 350 | 243 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| ZXXX-XXXXX-XX | ZetaFrame, Cable Port Opening for Top and Bottom Panels With Brush, Each | 3.9 | 8.8 | 34.32 |  | 273 | 175 | 121 | 546 | 350 | 243 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 39731-001 | Equipment Mounting Rail Grommet for 27.6"W (700 mm) and 29.5"W (750 mm) ZetaFrame Cabinet, Each | 1.5 | 5.3 | 7.9 |  | 63 | 40 | 28 | 126 | 80 | 56 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 39731-002 | Equipment Mounting Rail Grommet for 31.5"W (800 mm) ZetaFrame Cabinet, Each | 2.6 | 5.3 | 13.7 |  | 109 | 70 | 48 | 218 | 140 | 97 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 39716-001 | Equipment Mounting Rail Brush for 27.6"W (700 mm) and 29.5"W (750 mm) ZetaFrame Cabinet, Each | 1.6 | 5.5 | 8.8 |  | 70 | 45 | 31 | 140 | 90 | 62 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 39716-002 | Equipment Mounting Rail Brush for 31.5"W (800 mm) ZetaFrame Cabinet | 2.7 | 5.5 | 14.8 |  | 118 | 75 | 52 | 236 | 151 | 105 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 39774-XXX | ZetaFrame, Grommet Opening, Side Panel, Each | 3.9 | 8.8 | 34.3 |  | 273 | 175 | 121 | 546 | 349 | 243 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| GT-XXXXX | GT-Series GlobalFrame, Top Panel, Large Cable Port, Each | 3.9 | 8.9 | 34.71 |  | 276 | 177 | 123 | 552 | 354 | 246 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12035 | 25190-000 | Cable Port Brush Kit for CUBE-iT Wall-Mount Cabinet (each) | 8.8 | 1.95 | 17.1 |  | 136 | 87 | 60 | 272 | 174 | 121 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Z4-XXX-XXX-XXX | Z4-Series SeismicFrame, Cable Port, Top Panel, Each | 3.9 | 8.8 | 28 |  | 223 | 143 | 99 | 446 | 285 | 198 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Extended Fingers | Cable Opening (Per U) | Varies | 5.8 | 6.6 |  | 53 | 34 | 23 | 105 | 67 | 47 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Standard Fingers | Cable Opening (Per U) | Varies | 3.2 | 3.5 |  | 28 | 18 | 12 | 56 | 36 | 25 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| N-Series Fingers | Cable Opening (Per U) | Varies | 5.4 | 6.6 |  | 53 | 34 | 23 | 105 | 67 | 47 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Motive VCM | Cable Opening (Per U) | Varies | 5.4 | 6.6 |  | 53 | 34 | 23 | 105 | 67 | 47 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32697-00X | Cable Opening (Per U) with 1 Tool-less Bend Radius Installed | Varies | 5.4 | 5.8 |  | 46 | 30 | 21 | 92 | 59 | 41 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 32697-00X | Cable Opening (Per U) with 2 Tool-less Bend Radius Installed | Varies | 5.4 | 5.2 |  | 41 | 26 | 18 | 83 | 53 | 37 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Evolution VCM | Cable Opening (Per U) | Varies | 5.4 | 6.6 |  | 53 | 34 | 23 | 105 | 67 | 47 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Evolution HCM | Cable Opening (Per U) | Varies | 5.4 | 6.4 |  | 51 | 33 | 23 | 102 | 65 | 45 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Velocity VCM | Cable Opening (Per U) | Varies | 5.5 | 5.9 |  | 47 | 30 | 21 | 94 | 60 | 42 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Velocity HCM | Cable Opening (Per U) | Varies | 3.2 | 5.1 |  | 41 | 26 | 18 | 81 | 52 | 36 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Cable Runway Products | [11 empty] | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| (Maximum fill is equivalent to TIA recommended maximum fill - 6" deep cable at 50% fill. Order accessory cable retaining posts if cable height exceeds the height of the runway.) | [11 empty] | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 10250-X04 | Universal Cable Runway, 1.5"H x 4"W x 9'-11.5"L | 4.0 | 6.0 | 24 |  | 191 | 122 | 85 | 382 | 244 | 170 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 10250-X06 | Universal Cable Runway, 1.5"H x 6"W x 9'-11.5"L | 6.0 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 10250-X09 | Universal Cable Runway, 1.5"H x 9"W x 9'-11.5"L | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 10250-X12 | Universal Cable Runway, 1.5"H x 12"W x 9'-11.5"L | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 10250-X15 | Universal Cable Runway, 1.5"H x 15"W x 9'-11.5"L | 15.0 | 6.0 | 90 |  | 716 | 458 | 318 | 1432 | 917 | 637 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 10250-X18 | Universal Cable Runway, 1.5"H x 18"W x 9'-11.5"L | 18.0 | 6.0 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 10250-X24 | Universal Cable Runway, 1.5"H x 24"W x 9'-11.5"L | 24.0 | 6.0 | 144 |  | 1146 | 733 | 509 | 2292 | 1467 | 1019 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 10250-X31 | Universal Cable Runway, 1.5"H x 30"W x 9'-11.5"L | 30 | 6.0 | 180 |  | 1432 | 917 | 637 | 2865 | 1833 | 1273 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 10250-X37 | Universal Cable Runway, 1.5"H x 36"W x 9'-11.5"L | 36 | 6.0 | 216 |  | 1719 | 1100 | 764 | 3438 | 2200 | 1528 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 14300-X04 | Adjustable Cable Runway, 1.5" H x 4" W x 119.5" L (38 mm x 102 mm x 3035 mm) | 4 | 6 | 24 |  | 191 | 122 | 85 | 382 | 244 | 170 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 14300-X06 | Adjustable Cable Runway, 1.5" H x 6" W x 119.5" L (38 mm x 152 mm x 3035 mm) | 6 | 6 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10250 | 14300-X09 | Adjustable Cable Runway, 1.5" H x 9" W x 119.5" L (38 mm x 229 mm x 3035 mm) | 9 | 6 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10692 | 14300-X12 | Adjustable Cable Runway, 1.5" H x 12" W x 119.5" L (38 mm x 305 mm x 3035 mm | 12 | 6 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10692 | 14300-X15 | Adjustable Cable Runway, 1.5" H x 15" W x 119.5" L (38 mm x 381 mm x 3035 mm | 15 | 6 | 90 |  | 716 | 458 | 318 | 1432 | 917 | 637 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10692 | 14300-X18 | Adjustable Cable Runway, 1.5" H x 18" W x 119.5" L (38 mm x 457 mm x 3035 mm) | 18 | 6 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10692 | 14300-X24 | Adjustable Cable Runway, 1.5" H x 24" W x 119.5" L (38 mm x 610 mm x 3035 mm | 24 | 6 | 144 |  | 1146 | 733 | 509 | 2292 | 1467 | 1019 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10692 | 14300-X30 | Adjustable Cable Runway, 1.5" H x 30" W x 119.5" L (38 mm x 762 mmx 3035 mm) | 30 | 6 | 180 |  | 1432 | 917 | 637 | 2865 | 1833 | 1273 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10693 | 14300-X36 | Adjustable Cable Runway, 1.5" H x 36" W x 119.5" L (38 mm x 914 mm x 3035 mm) | 36 | 6 | 216 |  | 1719 | 1100 | 764 | 3438 | 2200 | 1528 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10693 | 14304-X04 | Tool-less Cross Member Radius Drop, Runway, 4" W (102 mm) | 2 | 1.4 | 2.8 |  | 22 | 14 | 10 | 45 | 29 | 20 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10693 | 14304-X06 | Tool-less Cross Member Radius Drop, Runway, 6" W (152 mm) | 4 | 1.4 | 5.6 |  | 45 | 29 | 20 | 89 | 57 | 40 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10693 | 14304-X09 | Tool-less Cross Member Radius Drop, Runway, 9" W (229 mm) | 6.2 | 1.4 | 8.7 |  | 69 | 44 | 31 | 138 | 89 | 62 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10693 | 14304-X12 | Tool-less Cross Member Radius Drop, Runway, 12" W (305 mm) | 9.2 | 1.4 | 12.9 |  | 103 | 66 | 46 | 205 | 131 | 91 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10723 | 14304-X15 | Tool-less Cross Member Radius Drop, Runway, 15" W (381 mm) | 12.2 | 1.4 | 17.1 |  | 136 | 87 | 60 | 272 | 174 | 121 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10723 | 14304-X18 | Tool-less Cross Member Radius Drop, Runway, 18" W (457 mm) | 15.2 | 1.4 | 21.3 |  | 169 | 108 | 75 | 339 | 217 | 151 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10723 | 14304-X24 | Tool-less Cross Member Radius Drop, Runway, 24" W (610 mm) | 21.2 | 1.4 | 29.7 |  | 236 | 151 | 105 | 473 | 303 | 210 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10723 | 14304-X30 | Tool-less Cross Member Radius Drop, Runway, 30" W (762 mm) | 27.2 | 1.4 | 38.1 |  | 303 | 194 | 135 | 606 | 388 | 270 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10723 | 14304-X36 | Tool-less Cross Member Radius Drop, Runway, 36" W (914 mm) | 33.2 | 1.4 | 46.5 |  | 370 | 237 | 164 | 740 | 474 | 329 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10723 | 14305-X00 | Tool-less Stringer Radius Drop, Runway, Large, 10.5" W (268 mm) | 7.8 | 1.4 | 11 |  | 88 | 56 | 39 | 175 | 112 | 78 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10723 | 14305-X01 | Tool-less Stringer Radius Drop, Runway, Small, 5.5" W (140 mm) | 3.6 | 1.4 | 5.1 |  | 41 | 26 | 18 | 81 | 52 | 36 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10724 | 10723-X04 | Cable Runway Outside Radius Bend, 4"W | 4 | 6.0 | 24 |  | 191 | 122 | 85 | 382 | 244 | 170 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10724 | 10723-X06 | Cable Runway Outside Radius Bend, 6"W | 6.0 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10724 | 10723-X08 | Cable Runway Outside Radius Bend, 8"W | 8 | 6.0 | 48 |  | 382 | 244 | 170 | 764 | 489 | 340 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10724 | 10723-X09 | Cable Runway Outside Radius Bend, 9"W | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10724 | 10723-X10 | Cable Runway Outside Radius Bend, 10"W | 10 | 6.0 | 60 |  | 477 | 306 | 212 | 955 | 611 | 424 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10724 | 10723-X12 | Cable Runway Outside Radius Bend, 12"W | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10724 | 10723-X15 | Cable Runway Outside Radius Bend, 15"W | 15.0 | 6.0 | 90 |  | 716 | 458 | 318 | 1432 | 917 | 637 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10723-X18 | Cable Runway Outside Radius Bend, 18"W | 18.0 | 6.0 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10723-X20 | Cable Runway Outside Radius Bend, 20"W | 20.0 | 6.0 | 120 |  | 955 | 611 | 424 | 1910 | 1222 | 849 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10723-X24 | Cable Runway Outside Radius Bend, 24"W | 24.0 | 6.0 | 144 |  | 1146 | 733 | 509 | 2292 | 1467 | 1019 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10723-X31 | Cable Runway Outside Radius Bend, 30"W | 30 | 6.0 | 180 |  | 1432 | 917 | 637 | 2865 | 1833 | 1273 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10723-X37 | Cable Runway Outside Radius Bend, 36"W | 36 | 6.0 | 216 |  | 1719 | 1100 | 764 | 3438 | 2200 | 1528 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X04 | Cable Runway Inside Radius Bend, 4"W | 4 | 6.0 | 24 |  | 191 | 122 | 85 | 382 | 244 | 170 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X06 | Cable Runway Inside Radius Bend, 6"W | 6.0 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X08 | Cable Runway Inside Radius Bend, 8"W | 8 | 6.0 | 48 |  | 382 | 244 | 170 | 764 | 489 | 340 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X09 | Cable Runway Inside Radius Bend, 9"W | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X10 | Cable Runway Inside Radius Bend, 10"W | 10 | 6.0 | 60 |  | 477 | 306 | 212 | 955 | 611 | 424 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X12 | Cable Runway Inside Radius Bend, 12"W | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X15 | Cable Runway Inside Radius Bend, 15"W | 15.0 | 6.0 | 90 |  | 716 | 458 | 318 | 1432 | 917 | 637 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
10822 | 10724-X18 | Cable Runway Inside Radius Bend, 18"W | 18.0 | 6.0 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10724-X20 | Cable Runway Inside Radius Bend, 20"W | 20.0 | 6.0 | 120 |  | 955 | 611 | 424 | 1910 | 1222 | 849 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10724-X24 | Cable Runway Inside Radius Bend, 24"W | 24.0 | 6.0 | 144 |  | 1146 | 733 | 509 | 2292 | 1467 | 1019 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10724-X31 | Cable Runway Inside Radius Bend, 30"W | 30 | 6.0 | 180 |  | 1432 | 917 | 637 | 2865 | 1833 | 1273 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10724-X37 | Cable Runway Inside Radius Bend, 36"W | 36 | 6.0 | 216 |  | 1719 | 1100 | 764 | 3438 | 2200 | 1528 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10822-X04 | Cable Runway E-Bend, 4"W | 4 | 6.0 | 24 |  | 191 | 122 | 85 | 382 | 244 | 170 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10822-X06 | Cable Runway E-Bend, 6"W | 6 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10822-X08 | Cable Runway E-Bend, 8"W | 8 | 6.0 | 48 |  | 382 | 244 | 170 | 764 | 489 | 340 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11252 | 10822-X09 | Cable Runway E-Bend, 9"W | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11275 | 10822-X09 | Cable Runway E-Bend, 9"W | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11275 | 10822-X10 | Cable Runway E-Bend, 10"W | 10 | 6.0 | 60 |  | 477 | 306 | 212 | 955 | 611 | 424 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11275 | 10822-X12 | Cable Runway E-Bend, 12"W | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11275 | 10822-X15 | Cable Runway E-Bend, 15"W | 15 | 6.0 | 90 |  | 716 | 458 | 318 | 1432 | 917 | 637 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11275 | 10822-X18 | Cable Runway E-Bend, 18"W | 18.0 | 6.0 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11275 | 10822-X20 | Cable Runway E-Bend, 20"W | 20 | 6.0 | 120 |  | 955 | 611 | 424 | 1910 | 1222 | 849 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
11275 | 10822-X24 | Cable Runway E-Bend, 24"W | 24 | 6.0 | 144 |  | 1146 | 733 | 509 | 2292 | 1467 | 1019 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12100 | 10822-X31 | Cable Runway E-Bend, 30"W | 30 | 6.0 | 180 |  | 1432 | 917 | 637 | 2865 | 1833 | 1273 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12100 | 10822-X37 | Cable Runway E-Bend, 36"W | 36 | 6.0 | 216 |  | 1719 | 1100 | 764 | 3438 | 2200 | 1528 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12100 | 11252-X06 | Telco Style Cable Runway, 1.5"H x 6"W x 8'-8.5"L | 6.0 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12100 | 11252-X09 | Telco Style Cable Runway, 1.5"H x 9"W x 8'-8.5"L | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12100 | 11252-X10 | Telco Style Cable Runway, 1.5"H x 10"W x 8'-8.5"L | 10.0 | 6.0 | 60 |  | 477 | 306 | 212 | 955 | 611 | 424 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12100 | 11252-X12 | Telco Style Cable Runway, 1.5"H x 12"W x 8'-8.5"L | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12100 | 11252-X13 | Telco Style Cable Runway, 1.5"H x 12"W x 4'-5.5"L | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12101 | 11252-X15 | Telco Style Cable Runway, 1.5"H x 15"W x 8'-8.5"L | 15.0 | 6.0 | 90 |  | 716 | 458 | 318 | 1432 | 917 | 637 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12101 | 11252-X18 | Telco Style Cable Runway, 1.5"H x 18"W x 8'-8.5"L | 18.0 | 6.0 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12101 | 11252-X20 | Telco Style Cable Runway, 1.5"H x 20"W x 8'-8.5"L | 20.0 | 6.0 | 120 |  | 955 | 611 | 424 | 1910 | 1222 | 849 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12170 | 11275-X06 | UL Classified Cable Rnwy,1.5"H x 6"W x 8'-8.5"L | 6.0 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12170 | 11275-X09 | UL Classified Cable Runway, 1.5"H x 9"W x 8'-8.5"L | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
12170 | 11275-X12 | UL Classified Cable Runway, 1.5"H x 12"W x 8'-8.5"L | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
31472 | 11275-X15 | UL Classified Cable Runway, 1.5"H x 15"W x 8'-8.5"L | 15.0 | 6.0 | 90 |  | 716 | 458 | 318 | 1432 | 917 | 637 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
31472 | 11275-X18 | UL Classified Cable Runway, 1.5"H x 18"W x 8'-8.5"L | 18.0 | 6.0 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
31472 | 11275-X20 | UL Classified Cable Runway, 1.5"H x 20"W x 8'-8.5"L | 20.0 | 6.0 | 120 |  | 955 | 611 | 424 | 1910 | 1222 | 849 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
31472 | 11275-X24 | UL Classified Cable Runway, 1.5"H x 24"W x 8'-8.5"L | 24.0 | 6.0 | 144 |  | 1146 | 733 | 509 | 2292 | 1467 | 1019 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12100-X06 | Cross Member Radius Drop, for 6"W Cable Runway | 3.0 | 1.4 | 4.2 |  | 33 | 21 | 15 | 67 | 43 | 30 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12100-X09 | Cross Member Radius Drop, for 9"W Cable Runway | 6.0 | 1.4 | 8.4 |  | 67 | 43 | 30 | 134 | 86 | 59 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12100-X12 | Cross Member Radius Drop, for 12"W Cable Runway | 8.0 | 1.4 | 11.2 |  | 89 | 57 | 40 | 178 | 114 | 79 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12100-X18 | Cross Member Radius Drop, for 18"W Cable Runway | 15.0 | 1.4 | 21 |  | 167 | 107 | 74 | 334 | 214 | 149 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12100-X07 | Radius Drop, for 9"W Movable Cross Member | 4.5 | 1.4 | 6.3 |  | 50 | 32 | 22 | 100 | 64 | 45 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12100-X10 | Radius Drop, for 12"W Movable Cross Member | 7.5 | 1.4 | 10.5 |  | 84 | 53 | 37 | 167 | 107 | 74 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12100-X16 | Radius Drop, for 18"W Movable Cross Member | 12.5 | 1.4 | 17.5 |  | 139 | 89 | 62 | 279 | 178 | 124 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12101-X01 | Stringer Radius Drop, for Universal Cable Runway | 7.3 | 1.4 | 10.2 |  | 81 | 52 | 36 | 162 | 104 | 72 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12101-X02 | Stringer Radius Drop, for Telco Cable Runway | 5.8 | 1.4 | 8.1 |  | 64 | 41 | 29 | 129 | 83 | 57 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12101-X03 | Stringer Radius Drop, for Cable Runway | 3.0 | 1.4 | 4.2 |  | 33 | 21 | 15 | 67 | 43 | 30 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12170-X06 | Quick Ship Cable Runway Kit, 1.5"H x 6"W x 4'-6"L | 6.0 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12170-X09 | Quick Ship Cable Runway Kit, 1.5"H x 9"W x 4'-6"L | 9.0 | 6.0 | 54 |  | 430 | 275 | 191 | 859 | 550 | 382 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 12170-X12 | Quick Ship Cable Runway Kit, 1.5"H x 12"W x 4'-6"L | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 31472-X06 | Alt Space Cable Runway, 1.5"H x 6"W x 8'-8.75"L | 6.0 | 6.0 | 36 |  | 286 | 183 | 127 | 573 | 367 | 255 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 31472-X12 | Alt Space Cable Runway, 1.5"H x 12"W x 8'-8.75"L | 12.0 | 6.0 | 72 |  | 573 | 367 | 255 | 1146 | 733 | 509 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 31472-X18 | Alt Space Cable Runway, 1.5"H x 18"W x 8'-8.75"L | 18.0 | 6.0 | 108 |  | 859 | 550 | 382 | 1719 | 1100 | 764 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| 31472-X24 | Alt Space Cable Runway, 1.5"H x 24"W x 8'-8.75"L | 24.0 | 6.0 | 144 |  | 1146 | 733 | 509 | 2292 | 1467 | 1019 | 0.031416 | 50% | 0.049087 | 50% | 0.070686 | 50% | 0.031416 | 100% | 0.049087 | 100% | 0.070686 | 100%
| Notes: | This table lists estimated cable fill for CPI cable management and pathway products. Cable fill varies with different cable sizes.
Cable fills are estimates based on .20" OD Cat 5e, .25" OD Cat 6, and .30" OD Cat 6a, 4-pair UTP horizontal cable. Cable fill varies with different size cables.
Use the Cat 5e value to estimate fill for 6-strand fiber. Use the Cat 6 value to estimate fill for 12-strand fiber.
Cable Runway/Tray Recommended/Maximum Cable Fills are based on TIA-569 recommendations and 5' (runway)/6' (tray) support spacing.
The (-X00) in part numbers is color or another variable that does not affect cable fill capacities. Refer to the CPI Mini-Catalog for available options.
To calculate recommended cable fills for other size cables, divide the product's usable area by the area of the cable and multiply by 25% (50% for maximum fill).
While every effort has been made to ensure the accuracy of all information, CPI does not accept liability for any errors or omissions and reserves the right to change
information and descriptions of listed services and products.
©2024 Chatsworth Products, Inc. All rights reserved. Chatsworth Products, Clik-Nut, CPI, CPI Passive Cooling, CUBE-iT, Secure Array, eConnect, Evolution, GlobalFrame, MegaFrame, QuadraRack, RMR, Saf-T-Grip, SeismicFrame, SlimFrame, TeraFrame, Motive, EuroFrame, Velocity and ZetaFrame are federally registered trademarks of Chatsworth Products. H-Plane, Hi-Bar, In-Plane, M-Frame, NetPoint, Oberon, Simply Efficient, Skybar, and Wi-Tile and are trademarks of Chatsworth Products. All other trademarks belong to their respective companies. 01/2024
Note on H6: CPI estimates cable fills with the following values: .20" OD for Cat 5e 4-pair UTP .25" OD for Cat 6 4-pair UTP .30" OD for Cat 6a 4-pair UTP Calculations assume round cables. Change the values to match your cable to estimate more accurate cable fills. Enter the outside diameter of the cable in inches.
Note on H7: Enter fill (how full) as a percentage. For vertical and horizontal cable managers: 50% fill is recommended for planning. 100% is the maximum fill. 100% fill returns the maximum number of loose cables that will fit in the manager at a 50% fill ratio. If you enter a fill that exceeds the maximum fill, the value for the maximum fill will be returned.

## MethodOfCalculation
Using the CPI CABLE FILL TABLE:
Change the OD (outside diameter) of the cable or the fill ratio on the table to estimate fills
for your application. Fill ratio is the percentage of Usable Area within the manager filled
with cable including gaps between cables.
Method of Calculation
Cable Fill is calculated by dividing the usable area of the cable manager by the area of the cable
and reducing by a 50% fill factor to allow for gaps between the cables.
The basic calculation for estimating recommended cable fill for cable managers and cable pathway is:
RECOMMENDED CABLE FILL = ((USABLE AREA/AREA OF CABLE) X 50%) X 50%
50% is the fill ratio (25% of the manager is filled with cable. 25% is required space between cables.)
The basic calculation for estimating maximum cable fill for cable managers and cable pathway is:
MAXIMUM CABLE FILL = (USABLE AREA/AREA OF CABLE) X 50%) X 100%
100% is the fill ratio. (50% of the manager is filled with cable. 50% is required air space between cables.)
USABLE AREA is the Usable Area of the cable manager or pathway product.
Usable Area is determined by measuring the internal width and
depth of individual cable managers or pathway as illustrated on the following pages.
The CPI Cable Fill table lists usable areas for CPI cable management and pathway products.
The area of a rectangular space is calculated by multiplying
the width by the depth. In some cases the width of the manager varries:
USABLE AREA = INTERIOR WIDTH X INTERIOR DEPTH
AREA OF CABLE is the area of the cable. The table assumes round cables.
The area of the cable is calculated using the dimensions of the cable.
To determine the values in the CPI Cable Fill table, average
cable sizes are used to represent each type of cable:
Cat 5e is .20" diameter cable (.031" area)
Cat 6 is .25" diameter cable (.049" area)
Cat 6a is .30" diameter cable (.070" area)
The area of a round cable is calculated by multiplying PI and
the diameter of the cable squared divided by 4:
(ROUND) CABLE AREA = (DIAMETER2 X PI)/4
FILL RATIO is the percentage of Usable Area within the manager that is filled with cable including
required gaps between cables.
CABLE FILL is the calculated cable fill value. This value is an estimate and includes gaps between
cables. Use 100% fill ratio to estimate maximum fill. Use 50% fill ratio to extimate initial fill.
This estimate represents loose cables, not bundled cables. The value will be less for bundled cables.
Sample Cable Fill Calculation:
Calculate cable fill of .30"OD Cat 6a UTP in CPI Cable Manager P/N 11730-703.
CPI P/N 11730-XXX has a usable area of 21.0 in2
.30" OD Cable has an area of .070 in² (Area = [.30]² X Pi/4)
RECOMMENDED CABLE FILL = ((USABLE AREA/AREA OF CABLE) X 50%) X 50%
RECOMMENDED CABLE FILL = (21.0 in²/.070 in²) X 50%) X 50%
RECOMMENDED CABLE FILL = 75 cables
MAXIMUM CABLE FILL = ((USABLE AREA/AREA OF CABLE) X 50%) X 100%
MAXIMUM CABLE FILL = (21.0 in²/.070 in²) X 50%) X 100%
MAXIMUM CABLE FILL = 150 cables
Usable Area defined for various types of cable managers.
The hatched areas represent the defined usable area for different types of CPI Cable Managers.
Vertical Cable Managers & Rings/Loops
(no fingers)
|  |  | Usable area is defined between | Ex. | VCS
|  |  | the narrowest point in width and |  | Loops
|  |  | the distance between the back |  | Rings
of the manager and the back of
the latch pins.
Latch pins
Vertical Cable Managers
(with fingers)
|  |  | Usable area is defined between | Ex. | MCS, MCS-EFX,
|  |  | the narrowest point in width and |  | CCS, CCS-EFX,
|  |  | the distance between the back |  | Velocity Cable Management
|  |  | of the manager and the back of |  | Evolution Cable Management
|  |  | the T on the fingers. |  | M-Series MegaFrame ECM
|  |  | Area includes this space. |  | F-Series TeraFrame VCM
GlobalFrame VCM
| Fingers |  |  |  | Finger Cable Manager
Motive Cable Management
Universal Horizontal Cable Managers
(with fingers)
|  |  | Usable area is defined between | Ex. | UHCM
|  |  | the narrowest point in height and |  | Velocity Cable Management
|  |  | the distance between the back |  | Evolution Cable Management
|  |  | of the manager and the back of |  | Motive Cable Management
the T on the fingers.
Fingers
Horizontal Wire Managers with Rings/Loops
(no fingers)
|  |  | Usable area is defined between | Ex. | Horz. Cble Mngr.
the narrowest point in height and
the distance between the back
of the manager and the front of
the rings.
Rings
Jumper Trays
(no fingers)
|  |  | Usable area is defined between | Ex. | Jumper Trays
the narrowest point in height and
the distance between the back
of the manager and the front of
the tray.
Cable Runway (& optional Cable Retaining Posts)
|  |  | Usable area is defined by the | Ex. | Universal
|  |  | width of the runway and a |  | TELCO
|  |  | maximum 6" height. |  | UL Classified
|  |  | TIA-569 limits cable height to |  | Alternate Space
|  |  | 6" (152 mm) and cable fill to 50%. |  | Quick Ship
Cable Runway does not have side walls.
Add Cable Retaining Post (shown) when required.
Pemsa® Rejiband® Wire Mesh Cable Tray
|  |  | Usable area is defined by the | Ex. | Rejiband
width of the tray and the height
of the tray, with a 6" (152 mm) max. height.
TIA-569 limits cable height to
6" (152 mm) and cable fill to 50%.
OnTrac Cable Tray has 2", 4" or 6" high (50 mm, 100 mm or 150 mm)
side walls.